# 3.1 – Safe elements of electrical isolation

Technical Guidance Series – VEU ceiling insulation activity

This is part of a series developed in conjunction with WorkSafe & Energy Safe Victoria to help installers in the VEU program to work safely while installing insulation.

Use this sheet and others in this series to plan safe series of work while installing insulation.

| VEU Ceiling Insulation – Technical Guidance Series |  |
| --- | --- |
| Working safely at heights |  |
| 1.1 | Working safely at heights during rooftop insulation installations |
| 1.2 | Edge protection – working at heights |
| 1.3 | Manual handling of heavy and bulky items |
| 1.4 | Working safely with ladders |
| 1.5 | Safe work practices using elevating work platforms |
| 1.6 | Falls through skylights, fragile roofs, voids and penetrations |
| Working safely in ceiling spaces |  |
| 2.1 | Working in pairs (best practice) |
| 2.2 | Working near asbestos containing material |
| 2.3 | Working with heat in ceiling spaces |
| 2.4 | Working in confined ceiling spaces |
| 2.5 | Falls through ceiling spaces |
| Working safely with electricity |  |
| 3.1 | Safe elements of electrical isolation (this sheet) |
| 3.2 | Safely isolating PV and battery systems |

## The importance of electrical isolation

When installing insulation, it’s vital to have a plan in place for safely isolating electrical circuits. This is especially important to ensure worker safety when inside the roof cavity due to the common presence of electrical wiring and connections to downlights, fans and other electrical appliances.

Additionally, solar and battery systems are now common on a lot of houses.

Electrocution is one of the leading causes of death for construction workers, including electricians. Each year, WorkSafe is notified of hundreds of electric shocks incidents, many of which occur during construction work.

During the Home Insulation Program (2009–2010), 3 workers died of electrocution in separate incidents. In two cases, metal staples penetrated reflective foil insulation and contacted electrical wiring, and in another incident a steel pole contacted a live conductor. Proper isolation of the electrical system would have prevented these fatalities.

Follow this 4-step risk management process to ensure hazards are identified, risks are assessed and controlled, and that employers fulfil their duty to monitor, review and revise controls when required:

Figure 1: The 4-step risk management process

## Step 1: Identify hazards

One of the key hazards when working in ceiling spaces is the risk of electric shock or electrocution.

Electric shock is the passage of electricity through the human body.

Electrocution is the passage of electricity through the human body which results in death.

Electrical wiring is commonly present in these areas and may be concealed beneath old insulation, run across joists and can be damaged or exposed.

It is essential to ensure that electrical systems are isolated before the works begin to ensure the risk of contact to live components is reduced.

Electric shock or electrocution occurs when an electrical current passes through the human body, which can conduct electricity. Depending on the severity and duration of exposure, contact with electricity can cause:

burns to the skin and internal tissues

disruption to the heart’s electrical activity, which may cause the heart to stop or beat irregularly.

Secondary risks, like falling from height.

Even in cases of seemingly minor exposure, medical attention should be sought to assess potential impacts on cardiac function.

Electrocution is one of the key risks when working in ceiling spaces, particularly when installing insulation.

During the Home Insulation Program, (2009-2010) 3 workers died of electrocution in separate incidents:

- In 2 instances, metal staples penetrated reflective foil insulation and contact was made with electrical wiring.

- In one instance, a steel pole was being used to move insulation into place when it made contact with a live wire.

In all these instances, proper isolation of the home electrical system would have prevented deaths.

## Step 2: Assess risks – electrocution in ceiling spaces

When working in ceiling spaces, there are several factors that increase the likelihood of an electrical hazard. This includes:

Vermin: Vermin such as mice, rats or possums can damage electrical wiring by chewing insulation. This can expose live conductors.

Worn electrical wiring insulation: Electrical wiring insulation can become brittle when it has deteriorated or been exposed to excessive heat. In addition, brittle insulation can break into pieces when disturbed. This can expose the live conductors.

Damage to the earth conductor or bonding: Hazards can develop from damage to the main earth conductor or earth electrode, or main neutral faults. This may cause current to flow in the earth conductors, or metallic parts such as metal pipes, exposing someone to a risk of electric shock or electrocution.

Previous electrical work: Non-compliant electrical work completed previously may increase the risk of electrocution, particularly where damaged cabling is installed through steel elements, creating the potential for steel components to become energised.

Reminder: if construction work relating to a ceiling space involves working on or near electrical installations or services, a safe work method statement (SWMS) must be prepared before work starts.

Employers and self-employed persons must ensure a safe work method statement (SWMS) is prepared before undertaking high-risk construction work (HRCW). A SWMS is a safety planning tool that identifies the hazards and risks of HRCW and documents the control measures necessary to manage those.

The SWMS needs to describe to employees in clear terms how risks from high-risk work will be effectively controlled to enable the work to be done safely. Consultation with employees involved in carrying out high-risk construction work must be part of the process of determining risk controls during the SWMS preparation process.

See the WorkSafe website for more information on when and how to complete a SWMS for construction activities: worksafe.vic.gov.au/safe-work-method-statements-swms

## Step 3: Control risks – safely isolating an electrical system

Follow these 5 steps to ensure electrical systems are safely isolated before work commences.

For more information about this topic, WorkSafe has produced a simple infographic summarising the isolation process: worksafe.vic.gov.au/resources/safe-elements-electrical-isolation

#### Step 3.1: Identify all sources of electricity

Before any work begins, you should identify:

all sources of electricity, including secondary supplies

the most appropriate point (or points) of the electrical installation to perform the isolation.

Sources of electricity in residential homes can include:

mains supply

generator back-ups

battery back-ups

control circuits

solar systems.

For further information regarding the correct process for safely isolating a PV systems, please refer to the following Step 3.2

#### Step 3.2: Isolate all sources of electricity

Isolate electrical equipment, installations and switchboards by turning off the main switches at the switchboard. Electric hot water systems and solar photovoltaic systems may have separate main switches. These should also be switched off.

As part of this process, it is important to understand the difference between de-energised and isolated.

De-energised means turning the electrical supply off (for example, at the main switch).

Isolated means turning the electrical supply off and locking out.

Isolation is a reasonably practicable step and a safer way to complete the work.

PVC tape or a cable tie attached to a circuit breaker, residual current device (RCD) or fuse is not effective isolation equipment. Using these may mean an electrical circuit can be re-energised. This could cause an electric shock or electrocution.

#### Step 3.3: Lock out the isolation point

Locking out a circuit breaker, RCD or fuses prevents them from being inadvertently energised. Use only devices that incorporate a lock or to which a lock can be added. These include:

padlocks

hasps

lock dogs.

The key to the lockout device must remain in the possession of the person who applied the lock and must not be shared. This prevents unauthorised removal of lockout and inadvertent re-energisation while work is being undertaken.

#### Step 3.4: Tag out the isolation point

Attach a tag to the switchboard that states:

who is working on the electrical installation

their contact information

item of plant

the reasons for isolation.

Tags can be printed or handwritten but must be clear and easy to read.

#### Step 3.5: Test the isolation is effective

Confirm that the isolation was effective by testing the electrical installation for voltage. This can include:

using an approved voltage tester to verify circuits are de-energised

proving the tester on a known live source before and after testing (test–prove–test)

testing at known electrical outlets, light fittings, or exposed conductors within the work area

checking multiple points within the ceiling space, as there may be more than one circuit present

confirming isolation at the switchboard (e.g. correct circuit breaker or fuse has been de-energised).

All wiring in ceiling spaces must be treated as always live, irrespective of any isolation measures undertaken.

## Step 4: Review and revise controls

Once isolation has been properly completed and verified, work may commence. However, employers need to remain vigilant to potential electrical hazards when operating in ceiling spaces. If the work method changes, new hazards are identified or the existing controls are no longer adequate, risk controls need to be reviewed and revised before work can continue.

All wiring should be treated as live after work has commenced, even where safe isolation has been confirmed.

Continuous awareness and adherence to electrical safety practices must be maintained throughout the task.

Where there is a change to the scope of work, work method, or site conditions, the SWMS must be reviewed, updated, and communicated to all affected workers prior to proceeding with the revised work activity.

Your actions shouldn't stop at Step 4. You should repeat this process often to make sure your management of risk is working.

© The State of Victoria Department of Energy, Environment and Climate Action September 2026.

ISBN 978-1-76176-982-5 (pdf/online/MS word)

Disclaimer

This publication may be of assistance to you but the State of Victoria and its employees do not guarantee that the publication is without flaw of any kind or is wholly appropriate for your particular purposes and therefore disclaims all liability for any error, loss or other consequence which may arise from you relying on any information in this publication.

Accessibility

To receive this publication in an alternative format, please contact the Victorian Energy Upgrades team at energy.upgrades@deeca.vic.gov.au. This document is also available on the internet at energy.vic.gov.au/victorian-energy-upgrades.

_______